## Cover
2006-11-08
PRODUCTS
Revision | No. | Contents
| 1 | Draft(06.11.08)
Nungwon Metal Ind. Co., Ltd.
☞

## Item
Korean Standard | Korean Standard | United States of America | Australia | Europe
KS Standard |  | ASTM | AS | BS EN
Standard | Tolerance | Standard | Standard | Standard
KS D5301 | Diameter Tolerance | ASTM B88 | AS1432 | BS EN1057
DWV | Thickness Tolerance | ASTM B280 | AS1571
ASTM B306
System Air Conditioner |  |  | Japan
PCC & LWC |  |  | Standard
ACR Tube |  |  | JIS H3300
Hexagonal, Octagonal TUBE
☞
☞
☞
☞
☞
☞
☞
☞
☞
☞
☞
☞
☞
☞

## KSD5301
Standard table of Plumbing tube
Use: Plumbing for water supply, water heating system, air conditioning and city gas
TYPE | Nominal size |  | Outer Diameter | Thickness | Tolerance | Weight | Pressure |  | Use
(kg/cm2)
| (A) | (B)(in) | (mm) | (mm) | (mm) | (kg/m) | Hard | Soft
K | 8 | 1/4 | 9.52 | 0.89 | ±0.13 | 0.216 | 111 | 71.6
| 10 | 3/8 | 12.7 | 1.24 | ±0.13 | 0.399 | 123 | 79.7
| 15 | 1/2 | 15.88 | 1.24 | ±0.15 | 0.51 | 95.3 | 61.6
| - | 5/8 | 19.05 | 1.24 | ±0.15 | 0.62 | 78.7 | 50.9
| 20 | 3/4 | 22.22 | 1.65 | ±0.18 | 0.593 | 90.8 | 58.7
| 35 | 1 | 28.58 | 1.65 | ±0.18 | 1.25 | 69.7 | 45.1 | * High pressure tube
| 32 | 11/4 | 34.92 | 1.65 | ±0.18 | 1.54 | 56.6 | 36.6 | * Medical use
| 40 | 11/2 | 41.28 | 1.83 | ±0.18 | 2.03 | 53.7 | 34.7 | * etc.
| 50 | 2 | 53.98 | 2.11 | ±0.25 | 3.07 | 46.1 | 29.8
| 65 | 2 1/2 | 66.68 | 2.41 | ±0.25 | 4.35 | 43.2 | 27.9
| 80 | 3 | 79.38 | 2.77 | ±0.25 | 5.96 | 42.4 | 27.4
| 90 | 3 1/2 | 92.08 | 3.05 | ±0.30 | 7.63 | 39.8 | 25.7
| 100 | 4 | 104.78 | 3.4 | ±0.35 | 9.68 | 38.7 | 25
| 125 | 5 | 130.18 | 4.06 | ±0.42 | 14.4 | 37.2 | 24
| 150 | 6 | 155.58 | 4.88 | ±0.42 | 20.7 | 38.1 | 24.7
| 200 | 8 | 206.38 | 6.88 | ±0.50 | 38.6 | 41.2 | 26.6
L | 8 | 1/4 | 9.52 | 0.76 | ±0.10 | 0.187 | 95.4 | 61.7
| 10 | 3/8 | 12.7 | 0.89 | ±0.13 | 0.295 | 81.7 | 52.8
| 15 | 1/2 | 15.88 | 1.02 | ±0.15 | 0.426 | 74.5 | 48.1
| - | 5/8 | 19.05 | 1.07 | ±0.15 | 0.54 | 65.3 | 42.2 | * Water supply
| 20 | 3/4 | 22.22 | 1.14 | ±0.15 | 0.675 | 60.1 | 38.8 | * Gas pipe
| 25 | 1 | 28.58 | 1.27 | ±0.15 | 0.974 | 52.6 | 34 | * Medical use
| 32 | 1 1/4 | 34.92 | 1.4 | ±0.15 | 1.32 | 47.9 | 31 | * fire extinguisher
| 40 | 1 1/2 | 41.28 | 1.52 | ±0.18 | 1.7 | 43.3 | 28 | * etc.
| 50 | 2 | 53.98 | 1.78 | ±0.22 | 2.61 | 38.5 | 24.9
| 65 | 2 1/2 | 66.68 | 2.03 | ±0.25 | 3.69 | 35.5 | 22.9
| 80 | 3 | 79.38 | 2.29 | ±0.25 | 4.96 | 34.1 | 22
| 90 | 3 1/2 | 92.08 | 2.54 | ±0.25 | 6.38 | 33 | 21.3
| 100 | 4 | 104.78 | 2.79 | ±0.30 | 7.99 | 31.5 | 20.4
| 125 | 5 | 130.18 | 3.18 | ±0.35 | 11.3 | 28.8 | 18.6
| 150 | 6 | 155.58 | 3.56 | ±0.35 | 15.2 | 27.3 | 17.6
| 200 | 8 | 206.38 | 5.08 | ±0.50 | 28.7 | 29.7 | 19.2
| 250 | 10 | 257.18 | 6.35 | ±0.50 | 44.7 | 29.8 | 19.2
M | 10 | 3/8 | 12.7 | 0.64 | ±0.10 | 0.217 | 57.2 | 37
| 15 | 1/2 | 15.88 | 0.71 | ±0.10 | 0.302 | 51.5 | 33.3
| 20 | 3/4 | 22.22 | 0.81 | ±0.15 | 0.487 | 39.6 | 25.6 | * Water supply
| 25 | 1 | 28.58 | 0.89 | ±0.15 | 0.692 | 34.4 | 22.2 | * Gas pipe
| 32 | 1 1/4 | 34.92 | 1.07 | ±0.15 | 1.02 | 35 | 22.6 | * Medical use
| 40 | 1 1/2 | 41.28 | 1.24 | ±0.15 | 1.39 | 35.1 | 22.7 | * fire extinguisher
| 50 | 2 | 59.98 | 1.47 | ±0.22 | 2.17 | 30.7 | 19.8 | * etc.
| 65 | 2 1/2 | 66.68 | 1.65 | ±0.22 | 3.01 | 28.4 | 18.3
| 80 | 3 | 79.38 | 1.83 | ±0.22 | 3.99 | 26.8 | 17.3
| 90 | 3 1/2 | 92.08 | 2.11 | ±0.25 | 5.33 | 26.7 | 17.3
| 100 | 4 | 104.78 | 2.41 | ±0.30 | 6.93 | 26.6 | 17.2
| 125 | 5 | 130.18 | 2.77 | ±0.30 | 9.91 | 25.1 | 16.2
| 150 | 6 | 155.58 | 3.1 | ±0.35 | 13.3 | 23.3 | 15.1
| 200 | 8 | 206.38 | 4.32 | ±0.45 | 24.5 | 24.8 | 16
| 250 | 10 | 257.18 | 5.38 | ±0.45 | 38.1 | 25 | 16.2
Seamless Copper Tube C 12200
☜

## KSD5301 (JIS)
A standard table of Plumbing tube
Use: Water supply, Air conditioner, City gas, Water heating system
TYPE | Nominal size |  | Outer Diameter | Thickness | Tolerance | Weight | Pressure |  | Use
(kg/cm2)
| (A) | (B)(in) | (mm) | (mm) | (mm) | (kg/m) | Hard | Soft
K | 8 | 1/4 | 9.52 | 0.89 | ±0.13 | 0.216 | 111 | 71.6
| 10 | 3/8 | 12.7 | 1.24 | ±0.13 | 0.399 | 123 | 79.7
| 15 | 1/2 | 15.88 | 1.24 | ±0.15 | 0.51 | 95.3 | 61.6
| - | 5/8 | 19.05 | 1.24 | ±0.15 | 0.62 | 78.7 | 50.9
| 20 | 3/4 | 22.22 | 1.65 | ±0.18 | 0.593 | 90.8 | 58.7
| 35 | 1 | 28.58 | 1.65 | ±0.18 | 1.25 | 69.7 | 45.1 | * High pressure tube
| 32 | 11/4 | 34.92 | 1.65 | ±0.18 | 1.54 | 56.6 | 36.6 | * Medical use
| 40 | 11/2 | 41.28 | 1.83 | ±0.18 | 2.03 | 53.7 | 34.7 | * etc.
| 50 | 2 | 53.98 | 2.11 | ±0.25 | 3.07 | 46.1 | 29.8
| 65 | 2 1/2 | 66.68 | 2.41 | ±0.25 | 4.35 | 43.2 | 27.9
| 80 | 3 | 79.38 | 2.77 | ±0.25 | 5.96 | 42.4 | 27.4
| 90 | 3 1/2 | 92.08 | 3.05 | ±0.30 | 7.63 | 39.8 | 25.7
| 100 | 4 | 104.78 | 3.4 | ±0.35 | 9.68 | 38.7 | 25
| 125 | 5 | 130.18 | 4.06 | ±0.42 | 14.4 | 37.2 | 24
| 150 | 6 | 155.58 | 4.88 | ±0.42 | 20.7 | 38.1 | 24.7
| 200 | 8 | 206.38 | 6.88 | ±0.50 | 38.6 | 41.2 | 26.6
L | 8 | 1/4 | 9.52 | 0.76 | ±0.10 | 0.187 | 95.4 | 61.7
| 10 | 3/8 | 12.7 | 0.89 | ±0.13 | 0.295 | 81.7 | 52.8
| 15 | 1/2 | 15.88 | 1.02 | ±0.15 | 0.426 | 74.5 | 48.1
| - | 5/8 | 19.05 | 1.07 | ±0.15 | 0.54 | 65.3 | 42.2 | * Water supply
| 20 | 3/4 | 22.22 | 1.14 | ±0.15 | 0.675 | 60.1 | 38.8 | * Gas pipe
| 25 | 1 | 28.58 | 1.27 | ±0.15 | 0.974 | 52.6 | 34 | * Medical use
| 32 | 1 1/4 | 34.92 | 1.4 | ±0.15 | 1.32 | 47.9 | 31 | * fire extinguisher
| 40 | 1 1/2 | 41.28 | 1.52 | ±0.18 | 1.7 | 43.3 | 28 | * etc.
| 50 | 2 | 53.98 | 1.78 | ±0.22 | 2.61 | 38.5 | 24.9
| 65 | 2 1/2 | 66.68 | 2.03 | ±0.25 | 3.69 | 35.5 | 22.9
| 80 | 3 | 79.38 | 2.29 | ±0.25 | 4.96 | 34.1 | 22
| 90 | 3 1/2 | 92.08 | 2.54 | ±0.25 | 6.38 | 33 | 21.3
| 100 | 4 | 104.78 | 2.79 | ±0.30 | 7.99 | 31.5 | 20.4
| 125 | 5 | 130.18 | 3.18 | ±0.35 | 11.3 | 28.8 | 18.6
| 150 | 6 | 155.58 | 3.56 | ±0.35 | 15.2 | 27.3 | 17.6
| 200 | 8 | 206.38 | 5.08 | ±0.50 | 28.7 | 29.7 | 19.2
| 250 | 10 | 257.18 | 6.35 | ±0.50 | 44.7 | 29.8 | 19.2
M | 10 | 3/8 | 12.7 | 0.64 | ±0.10 | 0.217 | 57.2 | 37
| 15 | 1/2 | 15.88 | 0.71 | ±0.10 | 0.302 | 51.5 | 33.3
| 20 | 3/4 | 22.22 | 0.81 | ±0.15 | 0.487 | 39.6 | 25.6 | * Water supply
| 25 | 1 | 28.58 | 0.89 | ±0.15 | 0.692 | 34.4 | 22.2 | * Gas pipe
| 32 | 1 1/4 | 34.92 | 1.07 | ±0.15 | 1.02 | 35 | 22.6 | * Medical use
| 40 | 1 1/2 | 41.28 | 1.24 | ±0.15 | 1.39 | 35.1 | 22.7 | * fire extinguisher
| 50 | 2 | 59.98 | 1.47 | ±0.22 | 2.17 | 30.7 | 19.8 | * etc.
| 65 | 2 1/2 | 66.68 | 1.65 | ±0.22 | 3.01 | 28.4 | 18.3
| 80 | 3 | 79.38 | 1.83 | ±0.22 | 3.99 | 26.8 | 17.3
| 90 | 3 1/2 | 92.08 | 2.11 | ±0.25 | 5.33 | 26.7 | 17.3
| 100 | 4 | 104.78 | 2.41 | ±0.30 | 6.93 | 26.6 | 17.2
| 125 | 5 | 130.18 | 2.77 | ±0.30 | 9.91 | 25.1 | 16.2
| 150 | 6 | 155.58 | 3.1 | ±0.35 | 13.3 | 23.3 | 15.1
| 200 | 8 | 206.38 | 4.32 | ±0.45 | 24.5 | 24.8 | 16
| 250 | 10 | 257.18 | 5.38 | ±0.45 | 38.1 | 25 | 16.2
Seamless Copper Tube C 12200
☜

## DWV
Chemical composition
Component | Min. | Max.
Copper % | 99.9 | -
Phosphorus % | 0.015 | 0.04
※ All items are produced as DHP based on C12200 standard.
Mechanical Properties
Type | Temper | Tensile strength,min
|  | ksiA | MpaB
Straight Tube | Hard | 40 | 275
A ksi = 1000 psi
B See Appendix
Please refer to the following standard.
NOMINAL SIZES |  | OD | THK | WEIGHT | TOLERANCE (mm)
(A) | (B) | (mm) | (mm) | (kg/m) | OD | THK
32 | 1.25 | 34.92 | 1.02 | 0.967 | 0.038 | 0.076
40 | 1.5 | 41.28 | 1.07 | 1.2 | 0.051 | 0.076
50 | 2 | 53.98 | 1.07 | 1.59 | 0.051 | 0.1
80 | 3 | 79.38 | 1.14 | 2.51 | 0.051 | 0.1
100 | 4 | 104.78 | 1.47 | 4.27 | 0.051 | 0.18
125 | 5 | 130.18 | 1.83 | 6.59 | 0.051 | 0.2
150 | 6 | 155.58 | 2.11 | 9.08 | 0.051 | 0.2
200 | 8 | 206.38 | 2.77 | 15.8 | 0.1 | 0.28
■ ASTM B 306(COPPER DRAINAGE TUBES)
☜

## Diameter Tolerance
TOLERANCE FOR AVERAGE DIAMETER
| TOLERANCE (mm) |  |  | TOLERANCE (mm)
| NORMAL | SPECIAL |  | NORMAL | SPECIAL
4 ( ∼ ) 15 | ±0.08 | ±0.05 | 100 ( ∼ ) 125 | ±0.27 | ±0.15
15 ( ∼ ) 25 | ±0.09 | ±0.06 | 125 ( ∼ ) 150 | ±0.35 | ±0.18
25 ( ∼ ) 50 | ±0.12 | ±0.08 | 150 ( ∼ ) 200 | ±0.50 | -
50 ( ∼ ) 75 | ±0.15 | ±0.10 | 200 ( ∼ ) 250 | ±0.65 | -
75 ( ∼ ) 100 | ±0.20 | ±0.13 | 250 ( ∼ ) 350 | ±0.40 | -
O.D or I.D
RANK
O.D or I.D
RANK
☜

## Thickness Tolerance
THICKNESS TOLERANCE
TOLERANCE (mm)
| 0.3 ~ | 0.4 ~ | 0.6 ~ | 0.8 ~ | 1.4 ~ | 2 ~ | 3 ~ | 4 ~ | 5.5 ~ | 7 ~
| 0.4 | 0.6 | 0.8 | 1.4 | 2 | 3 | 4 | 5.5 | 7
4 ∼ 15 | ±0.06 | ±0.07 | ±0.10 | ±0.13 | ±0.15 | ±0.18 | - | - | - | -
15 ∼ 25 | ±0.07 | ±0.08 | ±0.10 | ±0.15 | ±0.18 | ±0.20 | ±0.30 | ±0.40 | ±0.45 | -
25 ∼ 50 | - | ±0.09 | ±0.11 | ±0.15 | ±0.18 | ±0.20 | ±0.30 | ±0.40 | ±0.45 | ±8%
50 ∼ 100 | - | - | ±0.15 | ±0.18 | ±0.22 | ±0.25 | ±0.30 | ±0.40 | ±0.45 | ±8%
100 ∼ 175 | - | - | - | ±0.22 | ±0.25 | ±0.30 | ±0.35 | ±0.42 | ±0.45 | ±9%
175 ∼ 250 | - | - | - | - | ±0.30 | ±0.35 | ±0.40 | ±0.45 | ±0.50 | ±9%
■ Standard : KS D 5301, JIS H 3300, ASTM B 280 ■ ISO 9001, ■ QAS AS 1432 (Plumbing), AS/NZS 1571(ACR)
☜
O.D or I.D
RANK
RANK
(등급)

## SystemAirConditioner(LWC,PCC)
PCC & LWC (OL)
Item |  |  |  |  | Item
| OD | THK | Length | Packing |  | OD | THK | Length | Packing
PCC | 6.35 | 0.7 ~ 0.8 |  |  | LWC | 6.35 | 0.7 ~ 0.8
| 9.52 | 0.7 ~ 0.9 |  |  |  | 9.52 | 0.7 ~ 0.9
| 12.7 | 0.8 ~ 0.9 | 15M | Carton Box |  | 12.7 | 0.8 ~ 0.9
| 15.88 | 0.8 ~ 1.0 |  | Cap |  | 15.88 | 0.8 ~ 1.0 |  | Bobbin
| 19.05 | 0.8 ~ 1.0 | 30M |  |  | 19.05 | 0.8 ~ 1.0 |  | or Bulk
| 22.22 | 0.9 ~ 1.0 |  |  |  | 25.4 | 1.0 ~ 1.2
| 25.4 | 1.0 ~ 1.2 |  |  |  | 28.58 | 1.0 ~ 1.3
| 28.58 | 1.0 ~ 1.3
☜
RANK
(등급)
RANK
(등급)

## SystemAirConditioner(Straight)
Item | Outer Diameter | Thickness | Length | Packing
Straight Tube | 6.35 | 0.7 ~ 0.8 | 6M
| 9.52 | 0.7 ~ 0.9
| 12.7 | 0.8 ~ 0.9
| 15.88 | 0.8 ~ 1.0
| 19.05 | 0.8 ~ 1.0 |  | Cap
| 22.22 | 1.0 ~ 1.2 |  | Bundle with vinyl
| 25.4 | 1.0 ~ 1.2
| 28.58 | 1.0 ~ 1.3
| 31.75 | 1.3 ~ 1.4
| 38.1 | 1.4 ~ 1.52
| 44.45 | 1.7 ~ 1.78
☜

## ASTMB88
Chemical Composition
Composition | Min. | Max.
Copper,% | 99.9 | -
Phosphorus,% | 0.015 | 0.04
※The material shall conform to the following chemical requirements for Copper UNS No.C12200.
Mechanical Property Requirements
Temper Designation |  | Form | Rockwell HardnessA |  | Tensile strength, min,ksiB | Average Grain Size,min
Standard | Former |  | Scale | Value
O60 | annealed | coils | F | 50 max | 30 | 0.040 min
O50 | annealed | straight lengths | F | 55 max | 30 | 0.025 min
H58 | drawn | drawn | 30T | 30 min | 36 | …
A Rockwell hardness tests shall be made on the inside surfaces of the tube.When suitable equipment is not available for determiing the specified Rockwell hardness,other Rockwell scales and values shall be specified subject to agreement between the purchaser and the supplier.
B ksi = 1000 psi
Dimentions and Weights, and Tolerances in Diameter and Wall Thickness for Nominal or Standard Copper Water Tube Sizes
(All tolerances are plus and minus except as otherwise indicated)
Type K
Nominal or Standard Size,In. | Outside Diameter, In. | Average Outside DiameterA Tolerance,In. |  | Wall Thickness and Tolerance,In. |  | Theoretical Weight,ib/ft
|  | Annealed | Drawn | Wall Thickness | ToleranceB
1/4 | 0.375 | 0.002 | 0.001 | 0.035 | 0.0035 | 0.145
3/8 | 0.5 | 0.0025 | 0.001 | 0.049 | 0.005 | 0.269
1/2 | 0.625 | 0.0025 | 0.001 | 0.049 | 0.005 | 0.344
5/8 | 0.75 | 0.0025 | 0.001 | 0.049 | 0.005 | 0.418
3/4 | 0.875 | 0.003 | 0.001 | 0.065 | 0.006 | 0.641
1 | 1.125 | 0.0035 | 0.0015 | 0.065 | 0.006 | 0.839
1.25 | 1.375 | 0.004 | 0.0015 | 0.065 | 0.006 | 1.04
1.5 | 1.625 | 0.0045 | 0.002 | 0.072 | 0.007 | 1.36
2 | 2.125 | 0.005 | 0.002 | 0.083 | 0.008 | 2.06
2.5 | 2.625 | 0.005 | 0.002 | 0.095 | 0.01 | 2.93
3 | 3.125 | 0.005 | 0.002 | 0.109 | 0.011 | 4
3.5 | 3.625 | 0.005 | 0.002 | 0.12 | 0.012 | 5.12
4 | 4.125 | 0.005 | 0.002 | 0.134 | 0.013 | 6.51
5 | 5.125 | 0.005 | 0.002 | 0.16 | 0.016 | 9.67
6 | 6.125 | 0.005 | 0.002 | 0.192 | 0.019 | 13.9
8 | 8.125 | 0.006 | +0.002,-0.004 | 0.271 | 0.027 | 25.9
10 | 10.125 | 0.008 | +0.002,-0.006 | 0.338 | 0.034 | 40.3
12 | 12.125 | 0.008 | +0.002,-0.006 | 0.405 | 0.04 | 57.8
Type L
Nominal or Standard Size,In. | Outside Diameter, In. | Average Outer DiameterA Tolerance,In. |  | Wall Thickness and Tolerance,In. |  | Theoretical Weight,ib/ft
|  | Annealed | Drawn | Wall Thickness | ToleranceB
1/4 | 0.375 | 0.002 | 0.001 | 0.03 | 0.003 | 0.126
3/8 | 0.5 | 0.0025 | 0.001 | 0.035 | 0.004 | 0.198
1/2 | 0.625 | 0.0025 | 0.001 | 0.04 | 0.004 | 0.285
5/8 | 0.75 | 0.0025 | 0.001 | 0.042 | 0.004 | 0.362
3/4 | 0.875 | 0.003 | 0.001 | 0.045 | 0.004 | 0.455
1 | 1.125 | 0.0035 | 0.0015 | 0.05 | 0.005 | 0.655
1.25 | 1.375 | 0.004 | 0.0015 | 0.055 | 0.006 | 0.884
1.5 | 1.625 | 0.0045 | 0.002 | 0.06 | 0.006 | 1.14
2 | 2.125 | 0.005 | 0.002 | 0.07 | 0.007 | 1.75
2.5 | 2.625 | 0.005 | 0.002 | 0.08 | 0.008 | 2.48
3 | 3.125 | 0.005 | 0.002 | 0.09 | 0.009 | 3.33
3.5 | 3.625 | 0.005 | 0.002 | 0.1 | 0.01 | 0.29
4 | 4.125 | 0.005 | 0.002 | 0.114 | 0.011 | 5.38
5 | 5.125 | 0.005 | 0.002 | 0.125 | 0.012 | 7.61
6 | 6.125 | 0.005 | 0.002 | 0.14 | 0.014 | 10.2
8 | 8.125 | 0.006 | +0.002,-0.004 | 0.2 | 0.02 | 19.3
10 | 10.125 | 0.008 | +0.002,-0.006 | 0.25 | 0.025 | 30.1
12 | 12.125 | 0.008 | +0.002,-0.006 | 0.04 | 0.028 | 40.4
Type M
Nominal or Standard Size,In. | Outside Diameter, In. | Average Outer DiameterA Tolerance,In. |  | Wall Thickness and Tolerance,In. |  | Theoretical Weight,ib/ft
|  | Annealed | Drawn | Wall Thickness | ToleranceB
1/4 | 0.375 | 0.002 | 0.001 | § | § | §
3/8 | 0.5 | 0.0025 | 0.001 | 0.025 | 0.002 | 0.145
1/2 | 0.625 | 0.0025 | 0.001 | 0.028 | 0.003 | 0.204
5/8 | 0.75 | 0.0025 | 0.001 | § | § | §
3/4 | 0.875 | 0.003 | 0.001 | 0.032 | 0.003 | 0.328
1 | 1.125 | 0.0035 | 0.0015 | 0.035 | 0.004 | 0.465
1.25 | 1.375 | 0.004 | 0.0015 | 0.042 | 0.004 | 0.682
1.5 | 1.625 | 0.0045 | 0.002 | 0.049 | 0.005 | 0.94
2 | 2.125 | 0.005 | 0.002 | 0.058 | 0.006 | 1.46
2.5 | 2.625 | 0.005 | 0.002 | 0.065 | 0.006 | 2.03
3 | 3.125 | 0.005 | 0.002 | 0.072 | 0.007 | 2.68
3.5 | 3.625 | 0.005 | 0.002 | 0.083 | 0.008 | 3.58
4 | 4.125 | 0.005 | 0.002 | 0.095 | 0.01 | 4.66
5 | 5.125 | 0.005 | 0.002 | 0.109 | 0.011 | 6.66
6 | 6.125 | 0.005 | 0.002 | 0.122 | 0.012 | 8.92
8 | 8.125 | 0.006 | +0.002,-0.004 | 0.17 | 0.017 | 16.5
10 | 10.125 | 0.008 | +0.002,-0.006 | 0.212 | 0.021 | 25.6
12 | 12.125 | 0.008 | +0.002,-0.006 | 0.254 | 0.025 | 36.7
A The average outer diameter of a tube is the average of the maximum and minimum outer diameters as determined at any one cross section of the tube.
B Maximum deviation at any one point
C Indicates that the material is not generally available or that no tolerance has been established.
☜

## ASTMB306
Chemical Composition
Composition | Min. | Max.
Copper % | 99.9 | -
Phosphorus % | 0.015 | 0.04
※The material shall conform to the following chemical requirements for Copper UNS No.C12200.
Tensile Requirements
Form | Temper Designation |  | Tensile strength,min
| Standard | Former | ksiA | MpaB
Straight lengths | H58 | drawn general | 40 | 275
purpose
A ksi = 1000 psi
B See Appendix
Standard Dimensions,Weights,and Tolerances in Diameter and Wall Thickness
NOTE- All tolerances in this table are plus and minus except where otherwise noted
Nominal | Outer | Tolerance in | Wall Thickness, |  | Theoretical
Size, | Diameter | Average Outer | in.(mm) |  | Weight,
in. | in.(mm) | Diameter | Actual | Tolerance | lb/ft (kg/m)
1.25 | 1.375 (34.9) | 0.0015(0.038) | 0.040 (1.02) | 0.003 (0.076) | 0.650 (0.967)
1.5 | 1.625 (41.3) | 0.002 (0.051) | 0.042 (1.07) | 0.003 (0.076) | 0.809 (1.20)
2 | 2.125 (54.0) | 0.002 (0.051) | 0.042 (1.07) | 0.004 (0.10) | 1.07 (1.59)
3 | 3.125 (79.4) | 0.002 (0.051) | 0.045 (1.14) | 0.004 (0.10) | 1.69 (2.51)
4 | 4.125 (105) | 0.002 (0.051) | 0.058 (1.47) | 0.007 (0.18) | 2.87 (4.27)
5 | 5.125 (130) | 0.002 (0.051) | 0.072 (1.83) | 0.008 (0.20) | 4.43 (6.59)
6 | 6.125 (156) | 0.002 (0.051) | 0.083 (2.11) | 0.008 (0.20) | 6.10 (9.08)
8 | 8.125 (206) | +0.002 (0.051) | 0.109 (2.77) | 0.011 (0.28) | 10.6 (15.8)
-0.004 (0.10)
A The average outer diameter is the average,at any one cross section, of the maximum and minimum measured diameters(usually at or very close 90° to each other)
☜

## ASTMB280
Chemical Composition
Composition | Min. | Max.
Copper % | 99.9 | -
Phosphorus % | 0.015 | 0.04
※The material shall conform to the following chemical requirements for Copper UNS No.C12200.
Tensile Requirements
Form | Temper Designation |  | Tensile strength,min |  | Elongation in 2 in(50.8mm), min,%
| Standard | Former | ksiA | MpaB
Coiled length | O60 | soft annealed | 30 | 205 | 40
Straight lengths | H58 | drawn general | 36 | 250 | …
purpose
A ksi = 1000 psi
B See Appendix
Standard Dimentions and Weights,and Tolerances in Diameter and Wall Thickness for Coil Lengths
Standard Size ,In. | Outside Diameter in.(mm) | Wall Thickness in.(mm) | Weight,ib/ft(kg/m) | ToleranceB
|  |  |  | AverageA Outside Diameter Plus and Minus,in.(mm) | Wall Thickness,Plus and Minus,In.(mm)
1/8 | 0.125 (3.18) | 0.030 (0.762) | 0.0347 (0.0516) | 0.002 (0.051) | 0.003 (0.08)
3/16 | 0.187 (4.75) | 0.030 (0.762) | 0.0575(0.0856) | 0.002 (0.051) | 0.003 (0.08)
1/4 | 0.250 ( 6.35) | 0.030 (0.762) | 0.0804(0.120) | 0.002 (0.051) | 0.003 (0.08)
5/16 | 0.312 ( 7.92) | 0.032 (0.813) | 0.109(0.162) | 0.002 (0.051) | 0.003 (0.08)
3/8 | 0.375 ( 9.52) | 0.032 (0.813) | 0.134(0.199) | 0.002 (0.051) | 0.003 (0.08)
1/2 | 0.500 (12.70) | 0.032 (0.813) | 0.182(0.271) | 0.002 (0.051) | 0.003 (0.08)
5/8 | 0.625 (15.90) | 0.035 (0.889) | 0.251(0.373) | 0.002 (0.051) | 0.004 (0.10)
3/4 | 0.750 (19.10) | 0.035 (0.889) | 0.305(0.454) | 0.0025 (0.064) | 0.004 (0.10)
3/4 | 0.750 (19.10) | 0.042 (1.070) | 0.362(0.539) | 0.0025 (0.064) | 0.004 (0.10)
7/8 | 0.875 (22.20) | 0.045 (1.140) | 0.455(0.677) | 0.003 (0.076) | 0.004 (0.10)
1.125 | 1.125 (28.60) | 0.050 (1.270) | 0.665(0.975) | 0.0035 (0.089) | 0.005 (0.13)
1.375 | 1.375 (34.90) | 0.055 (1.40) | 0.884(1.32) | 0.004 (0.10) | 0.006 (0.15)
1.625 | 1.625 (41.30) | 0.060 (1.520) | 1.14(1.70) | 0.0045 (0.11) | 0.006 (0.15)
A The average outside diameter of a tube is the averageof the maximum and minimum outside diameters as determined at any one cross section of the tube.
B The tolerances listed represent the maximum deviation at any point
Standard Dimentions and Weights,and Tolerances in Diameter and Wall Thickness for Straight Lengths
NOTE- Applicable to drawn temper tube only
Standard Size ,In. | Outside Diameter in.(mm) | Wall Thickness in.(mm) | Weight,ib/ft(kg/m) | ToleranceB
|  |  |  | AverageA Outside Diameter Plus and Minus,in.(mm) | Wall Thickness,Plus and Minus,In.(mm)
3/8 | 0.375 ( 9.52) | 0.030 (0.762) | 0.126(0.187) | 0.001 (0.025) | 0.003 (0.08)
1/2 | 0.500 (12.70) | 0.035 (0.889) | 0.198(0.295) | 0.001 (0.025) | 0.004 (0.10)
5/8 | 0.625 (15.90) | 0.040 (1.020) | 0.285(0.424) | 0.001 (0.025) | 0.004 (0.10)
3/4 | 0.750 (19.10) | 0.042 (1.070) | 0.362(0.539) | 0.001 (0.025) | 0.004 (0.10)
7/8 | 0.875 (22.20) | 0.045 (1.140) | 0.455(0.677) | 0.001 (0.025) | 0.004 (0.10)
1.125 | 1.125 (28.60) | 0.050 (1.270) | 0.655(0.975) | 0.0015 (0.038) | 0.005 (0.13)
1.375 | 1.375 (34.90) | 0.055 (1.400) | 0.884(1.32) | 0.0015 (0.038) | 0.006 (0.15)
1.625 | 1.625 (41.30) | 0.060 (1.520) | 1.14(1.70) | 0.002 (0.051) | 0.006 (0.15)
2.125 | 2.125 (54.00) | 0.070 (1.780) | 1.75(2.60) | 0.002 (0.051) | 0.007 (0.18)
2.625 | 2.625 (66.70) | 0.080 (2.030) | 2.48(3.69) | 0.002 (0.051) | 0.008 (0.20)
3.125 | 3.125 (79.40) | 0.090 (2.290) | 3.33(4.96) | 0.002 (0.051) | 0.009 (0.23)
3.625 | 3.625 (92.10) | 0.100 (2.540) | 4.29(6.38) | 0.002 (0.051) | 0.010 (0.25)
4.125 | 4.125 (105.00) | 0.110 (2.790) | 5.38(8.01) | 0.002 (0.051) | 0.011 (0.28)
A The average outside diameter of a tube is the averageof the maximum and minimum outside diameters as determined at any one cross section of the tube.
B The tolerances listed represent the maximum deviation at any point
☜

## AS1432
CHEMICAL COMPOSION
Composition | Composition %
| Min. | Max.
Copper % | 99.9 | -
Phosphorus % | 0.015 | 0.04
DIMENSIONS OF TYPE A COPPER TUBES
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
Nominal size DN | Mean outside diameter mm |  |  | Ovality mm | Thickness mm
| Min. |  | Max. | Max.for straight lengths | Min.at any point | Nominal | Min.at any point
| Coils & LWP | Straight lengths
6 | 6.25 | 6.27 | 6.35 | 0.04 | 0.77 | 0.91 | 1.05
8 | 7.84 | 7.86 | 7.94 | 0.06 | 0.77 | 0.91 | 1.05
10 | 9.42 | 9.44 | 9.52 | 0.08 | 0.88 | 1.02 | 1.17
15 | 12.57 | 12.62 | 12.7 | 0.1 | 0.88 | 1.02 | 1.17
18 | 15.72 | 15.8 | 15.88 | 0.16 | 1.04 | 1.22 | 1.4
20 | 18.85 | 18.97 | 19.05 | 0.2 | 1.21 | 1.42 | 1.63
25 | 25.09 | 25.3 | 25.4 | 0.28 | 1.39 | 1.63 | 1.88
32 | 31.37 | 31.65 | 31.75 | 0.38 | 1.39 | 1.63 | 1.88
40 | 37.64 | 38 | 38.1 | 0.48 | 1.39 | 1.63 | 1.88
50 | - | 50.67 | 50.8 | 0.64 | 1.39 | 1.63 | 1.88
65 | - | 63.35 | 6.35 | 0.88 | 1.39 | 1.63 | 1.88
80 | - | 76.02 | 76.2 | 1.08 | 1.73 | 2.03 | 2.33
90 | - | 88.7 | 88.9 | 1.24 | 1.73 | 2.03 | 2.33
100 | - | 101.35 | 101.6 | 1.42 | 1.83 | 2.03 | 2.23
125 | - | 126.75 | 127 | 1.78 | 1.83 | 2.03 | 2.23
150 | - | 152.1 | 152.4 | 2.12 | 2.38 | 2.64 | 2.9
200 | - | 202.8 | 203.2 | 2.84 | 2.24 | 2.64 | 3.04
DIMENSIONS OF TYPE B COPPER TUBES
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
Nominal size DN | Mean outside diameter mm |  |  | Ovality mm | Thickness mm
| Min. |  | Max. | Max.for straight lengths | Min.at any point | Nominal | Min.at any point
| Coils & LWP | Straight lengths
6 | 6.25 | 6.27 | 6.35 | 0.04 | 0.6 | 0.71 | 0.82
8 | 7.84 | 7.86 | 7.94 | 0.06 | 0.6 | 0.71 | 0.82
10 | 9.42 | 9.44 | 9.52 | 0.08 | 0.77 | 0.91 | 1.05
15 | 12.57 | 12.62 | 12.7 | 0.1 | 0.77 | 0.91 | 1.05
18 | 15.72 | 15.8 | 15.88 | 0.16 | 0.88 | 1.02 | 1.17
20 | 18.85 | 18.97 | 19.05 | 0.2 | 0.88 | 1.02 | 1.17
25 | 25.09 | 25.3 | 25.4 | 0.28 | 1.04 | 1.22 | 1.4
32 | 31.37 | 31.65 | 31.75 | 0.38 | 1.04 | 1.22 | 1.4
40 | 37.64 | 38 | 38.1 | 0.48 | 1.04 | 1.22 | 1.4
50 | - | 50.67 | 50.8 | 0.64 | 1.04 | 1.22 | 1.4
65 | - | 63.35 | 6.35 | 0.88 | 1.04 | 1.22 | 1.4
80 | - | 76.02 | 76.2 | 1.08 | 1.39 | 1.63 | 1.88
90 | - | 88.7 | 88.9 | 1.24 | 1.39 | 1.63 | 1.88
100 | - | 101.35 | 101.6 | 1.42 | 1.47 | 1.63 | 1.79
125 | - | 126.75 | 127 | 1.78 | 1.47 | 1.63 | 1.79
150 | - | 152.1 | 152.4 | 2.12 | 1.83 | 2.03 | 2.23
200 | - | 202.8 | 203.2 | 2.84 | 1.78 | 2.03 | 2.28
DIMENSIONS OF TYPE C COPPER TUBES
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
Nominal size DN | Mean outside diameter mm |  |  | Ovality mm | Thickness mm
| Min. |  | Max. | Max.for straight lengths | Min.at any point | Nominal | Min.at any point
| Coils & LWP | Straight lengths
10 | 9.42 | 9.44 | 9.52 | 0.08 | 0.6 | 0.71 | 0.82
15 | 12.57 | 12.62 | 12.7 | 0.1 | 0.6 | 0.71 | 0.82
18 | 15.72 | 15.8 | 15.88 | 0.16 | 0.77 | 0.91 | 1.05
20 | 18.85 | 18.97 | 19.05 | 0.2 | 0.77 | 0.91 | 1.05
25 | 25.09 | 25.3 | 25.4 | 0.28 | 0.77 | 0.91 | 1.05
DIMENSIONS OF TYPE D COPPER TUBES
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
Nominal size DN | Mean outside diameter mm |  |  | Ovality mm | Thickness mm
| Min. |  | Max. | Max.for straight lengths | Min.at any point | Nominal | Min.at any point
| Coils & LWP | Straight lengths
32 | - | 31.65 | 31.75 | 0.38 | 0.77 | 0.91 | 1.05
40 | - | 38 | 38.1 | 0.48 | 0.77 | 0.91 | 1.05
50 | - | 50.67 | 50.8 | 0.64 | 0.77 | 0.91 | 1.05
65 | - | 63.35 | 63.5 | 0.88 | 0.77 | 0.91 | 1.05
80 | - | 76.02 | 76.2 | 1.08 | 1.04 | 1.22 | 1.4
90 | - | 88.7 | 88.9 | 1.24 | 1.04 | 1.22 | 1.4
100 | - | 101.35 | 101.6 | 1.42 | 1.09 | 1.22 | 1.35
125 | - | 126.75 | 127 | 1.78 | 1.27 | 1.42 | 1.57
150 | - | 152.1 | 152.4 | 2.12 | 1.47 | 1.63 | 1.79
TEMPER AND FORM
Thickness Type | Temper | Size range DN |  | Form
|  | Minimum | Maximum
| Hard drawn | 6 | 200 | Straight lengths
A | Bendable | 15 | 20 | Straight lengths
| Annealed | 6 | 40 | Coils & LWP
| Hard drawn | 6 | 200 | Straight lengths
B | Bendable | 15 | 20 | Straight lengths
| Annealed | 6 | 40 | Coils & LWP
| Hard drawn | 10 | 25 | Straight lengths
C | Bendable | 15 | 20 | Straight lengths
| Annealed | 10 | 25 | Coils & LWP
D | Hard drawn | 32 | 150 | Straight lengths
LENGTH TOLERANCE
Form |  | Specified length m |  | Tolerance
Straight lengths |  | ≤3 |  | +12,-0mm
|  | ＞3,≤6 |  | +24,-0mm
Coils |  | ≤15 |  | +300,-0mm
|  | ＞15 |  | +2,-0%
TUBE HARDNESS
Temper |  | Hardness,HV
|  | Min. | Max.
Hard drawn |  | 100 | -
Bendable |  | 80 | 100
Annealed |  | - | 70
☜

## ASNZS1571
CHEMICAL COMPOSION
Composition | Composition,Percent
| Min. | Max.
Copper(Including silver) % | 99.9 | -
Phosphorus % | 0.015 | 0.04
DIMENSIONAL TOLERANCES FOR OUTSIDE DIAMETER
Specified outside diameter | Tolerance*
| Straight lengths | Coils
＞3.18 ≤12.70 | +0, -0.08 | +0, -0.13
＞12.70 ≤19.05 | +0, -0.08 | +0, -0.20
＞19.05 ≤25.40 | +0, -0.08 | +0, -0.31
＞25.40 ≤31.75 | +0, -0.08 | +0, -0.38
＞31.75 ≤50.80 | +0, -0.08 | +0, -0.46
＞50.80 ≤101.60 | +0, -0.15 | -
＞101.60 ≤155.58 | +0, -0.30 | -
*Allowable deviation of mean outside diameter.
LENGTH TOLERANCE
Form of material | Specified length m | Length tolerance
Straight lengths | ≤2 | -0, +12 mm
| ＞2 ≤10 | -0, +24 mm
Coils | ≤15 | -0, +300 mm
| ＞15 | -0, +2 %
HARDNESS REQUIREMENTS
Temper | Vickness hardness,HV
| Min. | Max.
H | 100 | -
1/2H | 75 | 100
O | - | 75
☜

## BS EN 1057
Chemical Composition
Composition |  | Composition,Percent
|  | Min. |  | Max.
Copper (Including silver) % |  | 99.9 |  | 99.9
Phosphorus % |  | 0.015 |  | 0.015
Nominal outside diameters and thickness
Dimension in millimetres
Nominal outside diameter | Nominal wall thickness
d | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | 1.1 | 1.2 | 1.5 | 2 | 2.5 | 3
6 | x | R |  | R |  | R
8 | x | R |  | R |  | R
10 | x | R | R | R |  | R
12 | x | R | x | R |  | R
14 |  |  | x | x |  | x
15 | x |  | R | R |  | R |  | x | x
16 |  |  |  | x |  | x |  | x
18 |  | x |  | R |  | R |  | x | x
22 |  | x |  | x | R | R | x | R | R
25 | [5 empty] | x |  | x | x
28 |  | x |  | x | R | R |  | R | R
35 |  |  | x | x |  | x | x | R |  | x
40 | [5 empty] | x | x
42 |  |  |  | x |  | x |  | R | R | x
54 |  |  |  | x | x | x |  | R | R | R
64 | [8 empty] | x | R | x
66.7 | [5 empty] | x |  | R | x | x | x
70 | [9 empty] | x | x
76.1 | [7 empty] | x | R | R | x
80 | [5 empty] | x |  |  |  | x
88.9 | [9 empty] | R | x | x
108 | [7 empty] | x | R | x | R | x
133 | [8 empty] | R | x |  | R
159 | [8 empty] | x | R |  | R
219 | [11 empty] | R
267 | [11 empty] | R
R : indicates the European recommended dimensions
x : indicates other European dimensions
Nominal outside diameters and thickness
Dimension in millimetres
Nominal outside diameter d |  | Tolerances on outside diameters
|  | applicable to mean diameter |  | applicable to any diameter1)
over | up to and Including | all tempers |  | R290 (hard) temper |  | R250 (half hard) temper
62) | 18 | ±0.04 |  | ±0.04 |  | ±0.09
18 | 28 | ±0.05 |  | ±0.06 |  | ±0.10
28 | 54 | ±0.06 |  | ±0.07 |  | ±0.11
54 | 76.1 | ±0.07 |  | ±0.10 |  | ±0.15
76.1 | 88.9 | ±0.07 |  | ±0.15 |  | ±0.20
88.9 | 108 | ±0.07 |  | ±0.20 |  | ±0.30
108 | 159 | ±0.2 |  | ±0.7 |  | ±0.40
159 | 267 | ±0.6 |  | ±1.5 |  | -
1)Including devation from circular form
2)Including 6
NOTE.Tolerance for tubes in R220(annealed) temper are
applicable only to mean diameter
Tolerances on wall thickness
Dimension in millimetres
Nominal outside diameter d mm |  | Tolerances on wall thickness e1)
|  | e ＜ 1mm % |  | e ≥ 1mm %
＜ 18 |  | ±102) |  | ±13
≥ 18 |  | ±10 |  | ±152)
1)Including devation from concentricity
2)±10% for R250(half hard) tubes of 35mm,42mm and
54mm diameter with a wall thickness 1.2mm
NOTE.Concentricity(uniformity of wall thickness) is
controlled by tolerance on wall thickness
☜

## Hexagonal,Octagonal tube
NO. | TYPE | Hexagonal, Octagonal Tube standard size |  |  | Ref. | NO. | TYPE | Hexagonal, Octagonal Tube standard size |  |  | Ref.
|  | Vertex Length | Opposite Side Length | I.D. |  |  |  | Vertex Length | Opposite Side Length | I.D.
1 | Hexagon | 15.5 | 14 | 7.8 |  | 31 | Hexagon | 33.5 | 31.5 | 17.5
2 | Hexagon | 19 | 17.5 | 10.5 |  | 32 | Hexagon | 36 | 32 | 22.5
3 | Hexagon | 21 | 19 | 8.4 |  | 33 | Hexagon | 36.5 | 33.5 | 21.5
4 | Hexagon | 20.5 | 19 | 11.4 |  | 34 | Hexagon | 36.5 | 33.5 | 24.3
5 | Hexagon | 21 | 19 | 12.2 |  | 35 | Hexagon | 36.5 | 33.5 | 25
6 | Hexagon | 22 | 20 | 11.2 |  | 36 | Hexagon | 38.8 | 35 | 27
7 | Hexagon | 22 | 20 | 15 |  | 37 | Hexagon | 41.5 | 37.5 | 25.5
8 | Hexagon | 23 | 21 | 12 |  | 38 | Hexagon | 42.2 | 38 | 27
9 | Hexagon | 23 | 21 | 13.5
10 | Hexagon | 23 | 21 | 15 |  | 1 | Octagon | 36 | 32 | 19.5
11 | Hexagon | 25.5 | 24 | 12 |  | 2 | Octagon | 41 | 38.5 | 20.5
12 | Hexagon | 25.5 | 24 | 14 |  | 3 | Octagon | 41 | 38.5 | 25
14 | Hexagon | 25.5 | 24 | 15 |  | 4 | Octagon | 45 | 42 | 27.5
13 | Hexagon | 27 | 24 | 15 |  | 5 | Octagon | 45 | 42 | 28
15 | Hexagon | 27.9 | 25 | 15 |  | 6 | Octagon | 45 | 42 | 28
16 | Hexagon | 27.9 | 25 | 18 |  | 7 | Octagon | 45 | 42 | 31
17 | Hexagon | 27.5 | 25.5 | 13 |  | 8 | Octagon | 45 | 42 | 31
18 | Hexagon | 27.5 | 25.5 | 13.5 |  | 9 | Octagon | 45 | 42 | 33.5
19 | Hexagon | 27.5 | 25.5 | 14 |  | 10 | Octagon | 50 | 47 | 33.3
20 | Hexagon | 27.5 | 25.5 | 16.5 |  | 11 | Octagon | 52.3 | 49 | 34
21 | Hexagon | 27.5 | 25.5 | 17.5 |  | 12 | Octagon | 52.3 | 49 | 37.5
22 | Hexagon | 30 | 28 | 19 |  | 13 | Octagon | 57.5 | 54 | 40
23 | Hexagon | 30 | 28 | 19.3 |  | 14 | Octagon | 64 | 61 | 49.5
24 | Hexagon | 30 | 28 | 19.5 |  | 15 | Octagon | 64 | 61 | 49.5
25 | Hexagon | 30 | 28 | 20 |  | 16 | Octagon | 70 | 66.3 | 53
26 | Hexagon | 30 | 28 | 21 |  | 17 | Octagon | 79.5 | 74.7 | 61.5
27 | Hexagon | 33.4 | 30 | 21 |  | 18 | Octagon | 85.5 | 81 | 64.5
28 | Hexagon | 34 | 30.5 | 19 |  | 19 | Octagon | 94 | 89 | 75.8
29 | Hexagon | 33.5 | 30.5 | 20 |  | 20 | Octagon | 99.5 | 95 | 76.5
30 | Hexagon | 33.5 | 30.5 | 20.2 |  | 21 | Octagon | 120 | 115 | 101
Hexagonal, Octagonal Tube Standard Size
TUBE STANDARD SIZE
☜